## Map Standard
Modbus parameters: Holding register(16 bit), Signed, 38400 Baud, Character format: 8 data, No Parity, One stop
BACnet OBJECT ID | Menu Title | BACnet Values | Modbus Register # | Intac # | Menu | Modbus Values
1 | RH Set Point | 0-100 | 102 | 101 | 101 | 0 to 1000
2 | High Limit Set point | 0-100 | 103 | 102 | 102 | 0 to 1000
3 | RH Low Alarm | -0.1 to -100 | 104 | 103 | 103 | (-1) to -1000
4 | RH High Alarm | 0.1 to 100 | 105 | 104 | 104 | 1 to 1000
5 | Operation Mode | 0=Standby, 1=Normal, 2=Flush, 3=Forced Drain | 202 | 201 | 201 | 0=Standby, 1=Normal, 2=Flush, 3=Forced Drain
6 | Drain Duration Timer | 0 to 120 minutes | 203 | 202 | 202 | 0 to 120 minutes
7 | Drain Interval timer | 1 to 500 hours | 204 | 203 | 203 | 1 to 500 hours
8 | Cool Down Delay | 0 to 150 seconds | 205 | 204 | 204 | 0 to 150 seconds
9 | Cool Down Temp | 80-212 def F | 206 | 205 | 205 | 800-2120 def F
10 | Fill Delay Timer | 0-15 | 207 | 206 | 206 | 0-15
11 | Water Temp Set Point | 40-200 deg F | 208 | 207 | 207 | 400-2000 deg F
12 | Water Temp Hysteresis | 1-50 deg F | 209 | 208 | 208 | 10-500 deg F
13 | End of Use Drain Timer | 0-168 hours | 210 | 209 | 209 | 0-168 hours
14 | Time to Clean Timer | 0-365 days | 211 | 210 | 210 | 0-365 days
15 | Clean Reset | 0=off, 1=on | 212 | 211 | 211 | 0=off, 1=on
16 | Intac Address | 1-247 modbus (read only) | 213 | 212 | 212 | 1-247 modbus (read only)
17 | Intac Baud Rate | 0=9600, 1=19200, 2=38400 | 214 | 213 | 213 | 0=9600, 1=19200, 2=38400
18 | Room Prop band | 0 to 1000 | 302 | 301 | 301 | 0 to 1000
19 | Room hysteresis | 1 to 500 | 303 | 302 | 302 | 1 to 500
20 | Room Integral | 0 to 6000 | 304 | 303 | 303 | 0 to 6000
21 | Room Derivative | 0 to 999 | 305 | 304 | 304 | 0 to 999
22 | Cycle Time | 1 to 10 for SCR/SCRmod, 30 to 240 for TCM | 306 | 305 | 305 | 1 to 10 for SCR/SCRmod, 30 to 240 for TCM
23 | Duct Prop Band | 0 to 1000 | 307 | 306 | 306 | 0 to 1000
24 | Duct Hysteresis | 1 to 500 | 308 | 307 | 307 | 1 to 500
25 | Duct Integral | 0 to 999 | 309 | 308 | 308 | 0 to 999
26 | Duct Derivative | 0 to 999 | 310 | 309 | 309 | 0 to 999
27 | RH Input filter | 0-60 | 311 | 310 | 310 | 0-60
28 | Control Source | 0=Transmitter, 1=Process Signal | 503 | 502 | 502 | 0=Transmitter, 1=Process Signal
29 | Water Sensor | 0=None, 1=J type, 2= K type, 3=T Type | 504 | 503 | 503 | 0=None, 1=J type, 2= K type, 3=T Type
30 | RH Sensor | 4=current, 5=Voltage | 505 | 504 | 504 | 4=current, 5=Voltage
31 | RH Process Low | 0 to 20.00 for mA, 0-10.00 for VDC | 506 | 505 | 505 | 0 to 2000 for mA, 0-1000 for VDC
32 | RH Process High | 0 to 20.00 for mA, 0-10.00 for VDC | 507 | 506 | 506 | 0 to 2000 for mA, 0-1000 for VDC
33 | High Limit Sensor | 0=None, 4=mA, 5=VDC | 509 | 508 | 508 | 0=None, 4=mA, 5=VDC
34 | HighLimit Process Low | 0 to 20.00 for mA, 0-10.00 for VDC | 510 | 509 | 509 | 0 to 2000 for mA, 0-1000 for VDC
35 | HighLimit Process High | 0 to 20.00 for mA, 0-10.00 for VDC | 511 | 510 | 510 | 0 to 2000 for mA, 0-1000 for VDC
36 | Outdoor Air Sensor | 0=None, 4=mA | 512 | 511 | 511 | 0=None, 4=mA
37 | OAT Process Low | 2.00 to 20.00 mA | 513 | 512 | 512 | 200 to 2000 mA
38 | OAT Process High | 2.00 to 2.000 mA | 514 | 513 | 513 | 200 to 2000 mA
39 | OAT Range Low | (-100.0) to 1000.0 | 515 | 514 | 514 | (-1000) to 10000
40 | OAT Range High | (-100.0) to 1000.0 | 516 | 515 | 515 | (-1000) to 10000
41 | OAT Offset | 0 to 60.0 | 517 | 516 | 516 | 0 to 600
42 | Process Output | 0=Volts, 1=mA | 518 | 517 | 517 | 0=Volts, 1=mA
43 | Out Process Low | 0 to 3.00 for VDC, 0 to 8.00mA | 519 | 518 | 518 | 0 to 300 for VDC, 0 to 800mA
44 | Out Process High | 3.00 to 10.00 for VDC, 10.00 to 20.00 for mA | 520 | 519 | 519 | 300 to 1000 for VDC, 1000 to 2000 for mA
45 | Dedicated Input | 0=Not Used, 1=Panel Lockout, 2=dedicated event, 3=High limit open, 4=Autodrain | 521 | 520 | 520 | 0=Not Used, 1=Panel Lockout, 2=dedicated event, 3=High limit open, 4=Autodrain
46 | Temp units | 0=Fahrenheit, 1=Celsius | 522 | 521 | 521 | 0=Fahrenheit, 1=Celsius
47 | Capacity Units | 0=lbs./hr, 1=kg/hr | 523 | 522 | 522 | 0=lbs./hr, 1=kg/hr
48 | Unit Capacity | 2 to 9999 | 524 | 523 | 523 | 2 to 9999
49 | Menu access | 0=100 menu, 1=100/200 menu, 2=All menus, 3=No menus | 526 | 525 | 525 | 0=100 menu, 1=100/200 menu, 2=All menus, 3=No menus
50 | Control Type | 0=TCM, 1=On/Off, 2=SCR, 3=Steam, 4=gas, 5=SCRmod | 702 | 701 | 701 | 0=TCM, 1=On/Off, 2=SCR, 3=Steam, 4=gas, 5=SCRmod
51 | Active heaters | 1 to 4 for high end, 1 only for low end | 703 | 702 | 702 | 1 to 4 for high end, 1 only for low end
52 | Water Enable | 0=off, 1=on | 704 | 703 | 703 | 0=off, 1=on
53 | Air Enable | 0=off, 1=on | 705 | 704 | 704 | 0=off, 1=on
54 | Water Level Sensor | 0=Triprobe, 1=float, 2=none | 706 | 705 | 705 | 0=Triprobe, 1=float, 2=none
55 | Drain Type | 0=Manual, 1=Automatic, 2=None | 707 | 706 | 706 | 0=Manual, 1=Automatic, 2=None
56 | High limit enable | 0=off, 1=on | 708 | 707 | 707 | 0=off, 1=on
57 | Clean Time | 0=elapsed time, 1=accum time, 2=on demand | 709 | 708 | 708 | 0=elapsed time, 1=accum time, 2=on demand
58 | Gas Burners | 1 to 3 | 710 | 709 | 709 | 1 to 3
59 | Low Fire Set point | 5 to 100 | 711 | 710 | 710 | 5 to 100
60 | Low Fire Hysteresis | 1 to 99 | 712 | 711 | 711 | 1 to 99
61 | Burner #2 Set point | 5 to 100 | 713 | 712 | 712 | 5 to 100
62 | Burner #2 Hysteresis | 1 to 99 | 714 | 713 | 713 | 1 to 99
63 | Burner #3 Set Point | 5 to 100 | 715 | 714 | 714 | 5 to 100
64 | Burner #3 Hysteresis | 1 to 99 | 716 | 715 | 715 | 1 to 99
65 | Post purge timer | 5 to 999 seconds | 717 | 716 | 716 | 5 to 999 seconds
66 | VFD Intensity | 1 to 8 | 718 | 717 | 717 | 1 to 8
67 | Range Checking | 0=off, 1=on | 719 | 718 | 718 | 0=off, 1=on
68 | Low H2O Timer | 0 to 15 seconds | 720 | 719 | 719 | 0 to 15 seconds
69 | Actual Humidity | 0-100 | 49 | 48 | 001 | 0-1000, implied tenths
70 | Control RH Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 50 | 49 | E03 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
71 | High Limit RH Actual | 0-100 | 51 | 50 | 006 | 0-1000
72 | High Limit RH Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 52 | 51 | E04 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
73 | Water Temp Actual | -13 to 266 | 53 | 52 | 008 | -130- 2660, implied tenths
74 | Water Sensor(temp) | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 54 | 53 | E06 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
75 | Outdoor Air Temp Actual | -100 to 1000 | 55 | 54 | 009 | -1000-10,000 implied tenths
76 | Outdoor Air Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 56 | 55 | E05 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
77 | Heater #1 %Power | 0-100 | 823 | 822 | none | 0-100
78 | Heater #2 %Power | 0-100 | 824 | 823 | none | 0-100
79 | Heater #3 %Power | 0-100 | 825 | 824 | none | 0-100
80 | Heater #4 %Power | 0-100 | 826 | 825 | none | 0-100
81 | Heater Power | 0-100 | 853 | 852 | 002 | 0-100
82 | Water Level | 0=No error, 1=bad tri-probe, 2=Fill fault, 3= Refill fault, 4=Low float, 5=Low, 6=Drain fault | 831 | 830 | E07 | 0=No error, 1=bad tri-probe, 2=Fill fault, 3= Refill fault, 4=Low float, 5=Low, 6=Drain fault
83 | Accumulated Run Time | 0-365 days | 852 | 851 | 012 | 0-365 days
84 | Internal Module #1 I/O Error | 0=no, 1=yes | 847 | 846 | E08 | 0=no, 1=yes
85 | Internal Module #2 I/O Error | 0=no, 1=yes | 848 | 847 | E08 | 0=no, 1=yes
86 | Internal Module #3 I/O Error | 0=no, 1=yes | 849 | 848 | E08 | 0=no, 1=yes
87 | Interlock Input Open | 0=safety circuit open( error condition), 1=Safety circuit closed(safeties satisfied) | 857 | 856 | E01 | 0=safety circuit open( error condition), 1=Safety circuit closed(safeties satisfied)
88 | Dedicated Input | 0=open contact, 1=closed contact | 858 | 857 | E02 | 0=open contact, 1=closed contact
89 | Actual Water Level | 4=Full, 3=Normal=, 2 =Refill 1=Low, 0= Error | 832 | 831 | none | 4=Full, 3=Normal=, 2 =Refill 1=Low, 0= Error
90 | Fill Status | 0=off, 1=on | 840 | 839 | none | 0=off, 1=on

## Map with CLICK
Modbus parameters: Holding register(16 bit), Signed, 38400 Baud, Character format: 8 data, No Parity, One stop
BACnet OBJECT ID | Menu Title | BACnet Values | Modbus Register # | Intac # | Menu | Modbus Values
1 | RH Set Point | 0-100 | 102 | 101 | 101 | 0 to 1000
2 | High Limit Set point | 0-100 | 103 | 102 | 102 | 0 to 1000
3 | Operation Mode | 0=Standby, 1=Normal, 2=Flush, 3=Forced Drain | 202 | 201 | 201 | 0=Standby, 1=Normal, 2=Flush, 3=Forced Drain
4 | Actual Humidity | 0-100 | 49 | 48 | 001 | 0-1000, implied tenths
5 | Control RH Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 50 | 49 | E03 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
6 | High Limit RH Actual | 0-100 | 51 | 50 | 006 | 0-1000
7 | High Limit RH Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 52 | 51 | E04 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
8 | Water Temp Actual | -13 to 266 | 53 | 52 | 008 | -130- 2660, implied tenths
9 | Water Sensor(temp) | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 54 | 53 | E06 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
10 | Outdoor Air Temp Actual | -100 to 1000 | 55 | 54 | 009 | -1000-10,000 implied tenths
11 | Outdoor Air Sensor | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow | 56 | 55 | E05 | 0=No Error, 1= Under range, 2= Over range, 3=Underflow, 4=Overflow
12 | Heater #1 %Power | 0-100 | 823 | 822 | none | 0-100
13 | Heater #2 %Power | 0-100 | 824 | 823 | none | 0-100
14 | Heater #3 %Power | 0-100 | 825 | 824 | none | 0-100
15 | Heater #4 %Power | 0-100 | 826 | 825 | none | 0-100
16 | Heater Power | 0-100 | 853 | 852 | 002 | 0-100
17 | Water Level | 0=No error, 1=bad tri-probe, 2=Fill fault, 3= Refill fault, 4=Low float, 5=Low, 6=Drain fault | 831 | 830 | E07 | 0=No error, 1=bad tri-probe, 2=Fill fault, 3= Refill fault, 4=Low float, 5=Low, 6=Drain fault
18 | Accumulated Run Time | 0-365 days | 852 | 851 | 012 | 0-365 days
19 | Internal Module #1 I/O Error | 0=no, 1=yes | 847 | 846 | E08 | 0=no, 1=yes
20 | Internal Module #2 I/O Error | 0=no, 1=yes | 848 | 847 | E08 | 0=no, 1=yes
21 | Internal Module #3 I/O Error | 0=no, 1=yes | 849 | 848 | E08 | 0=no, 1=yes
22 | Interlock Input Open | 0=safety circuit open( error condition), 1=Safety circuit closed(safeties satisfied) | 857 | 856 | E01 | 0=safety circuit open( error condition), 1=Safety circuit closed(safeties satisfied)
23 | Dedicated Input | 0=open contact, 1=closed contact | 858 | 857 | E02 | 0=open contact, 1=closed contact
24 | Actual Water Level | 4=Full, 3=Normal=, 2 =Refill 1=Low, 0= Error | 832 | 831 | none | 4=Full, 3=Normal=, 2 =Refill 1=Low, 0= Error
25 | Fill Status | 0=off, 1=on | 840 | 839 | none | 0=off, 1=on
26 | Write RH SetPoint | 0-100
27 | Write High Limit Set Point | 0-100
28 | Write Operation Mode | 0=Standby, 1=Normal, 2=Flush, 3=Forced Drain
29 | Burner Lockout Alarm | 0=off, 1=on

## CLICK
Holding register
RH Set Point | AV | 1 | 45
High Limit Set point | AV | 2 | 46
Operation Mode | AV | 3 | 47
Actual Humidity | AV | 4 | 37
Control RH Sensor | AV | 5 | 38
High Limit RH Actual | AV | 6 | 39
High Limit RH Sensor | AV | 7 | 40
Water Temp Actual | AV | 8 | 41
Water Sensor(temp) | AV | 9 | 42
Outdoor Air Temp Actual | AV | 10 | 43
Outdoor Air Sensor | AV | 11 | 44
Heater #1 %Power | AV | 12 | 1
Heater #2 %Power | AV | 13 | 2
Heater #3 %Power | AV | 14 | 3
Heater #4 %Power | AV | 15 | 4
Heater Power | AV | 16 | 31
Water Level | AV | 17 | 9
Accumulated Run Time | AV | 18 | 30
Internal Module #1 I/O Error | AV | 19 | 25
Internal Module #2 I/O Error | AV | 20 | 26
Internal Module #3 I/O Error | AV | 21 | 27
Interlock Input Open | AV | 22 | 35
Dedicated Input | AV | 23 | 36
Actual Water Level | AV | 24 | 10
Fill Valve Status | AV | 25 | 18
Write RH SetPoint | AV | 26 | 2045
Write High Limit Set Point | AV | 27 | 2046
Write Operation Mode | AV | 28 | 2047