**PURE Humidifier Co.**

**Sample Specification**

**Atmospheric Steam Insty-Pac Series**

The humidifier shall be capable of removing condensate from the steam by means of a 304L stainless steel supply header/separator, for the purpose of providing condensate free steam.

The header/separator shall be designed with an internal baffle to assure equal steam flow to the injection tubes. The header/separator shall include an internal stainless steel screen to prevent objectionable noise due to pressure drop across the valve.

Steam shall be injected into the air stream through round 304L stainless steel steam jacketed injection tubes. The tubes shall be steam jacketed to assure condensate-free vapor. The jacketing shall only be hot during a call for humidity, eliminating unwanted heat gain when no humidification is required. The steam emission ports shall be precision punched and shall be of sufficient size and number to provide constant and uniform distribution of steam over the entire width of the duct.

The injection tubes shall be completely factory assembled and welded to a 304L stainless steel header/separator, ready for installation and piping connections.

The assembly shall be an all welded design eliminating the use of o-rings and couplings that may cause leakage and ongoing maintenance.

The humidifier shall be designed so that only one side of the AHU/duct is accessed for supply and condensate piping. An air blank-off plate shall not be required.

The humidifier shall be a PURE Humidifier Co. humidifier as manufactured by PURE Humidifier Co., Chaska, Minnesota.